## Template3
Project Name: | Enter your data
Unit: | Geniox Tera C Macro CRAH
Model: | TERA 170
Unit summary |  |  | Version 1.1.0.0
Configuration |  |  | TOP RETURN BOTTOM SUPPLY
Cooling capacity |  |  | 340.7
Airflow |  |  | 33333
Supply/Return air temperature |  |  | 14.2/44
Power supply |  |  | 400V-3PH-N-PE-50Hz
Dimensions (W x L x H) |  |  | 4082 x 1082 x 3200 mm
Casing/Frame Details
Panel Thickness |  |  | 60 mm
Panel Insulation Type / Density |  |  | Rock wool 60kg/m3
Panel External Sheet |  |  | Z275 Steel + Polyster Painted (0,8mm)
Panel Internal Sheet |  |  | Z275 Steel + Polyster Painted (0,8mm)
Frame Type |  |  | Z275 + Epoxy Primer Polyester Painted Steel
Water Cooling Coil Details
Fluid |  | WATER |  | %
Return Air Temparature |  | 44 |  | °C
Return Air Humidity |  | 11 |  | %
Supply Air Temparature |  | 14.2 |  | °C
Supply Air Humidity |  | 62.2 |  | %
Coil Pressure Drop (Air side) |  | 102.8 |  | Pa
Coil Cooling Capacity |  | 340.7 |  | kW
Fluid Inlet Temparature. |  | 11 |  | °C
Fluid Outlet Temparature |  | 22 |  | °C
Water Flow Rate |  | 26.6 |  | m³/h
Coil Pressure Drop (Fluid side) |  | 85.8 |  | kPa
EER (Energy Efficiency Ratio) |  | 71
Connections (Inlet-Outlet) |  | DN 80
Air density |  |  |  | kg/m³
Supply Fan Details
Air Flow Rate |  | 33333 |  | m³/h
External Pressure |  | 111 |  | Pa
Total Static Pressure |  | 259.3 |  | Pa
Fan Speed |  | 1513 |  | rpm
Maximum Fan Speed |  | 2370 |  | rpm
Total Efficiency |  | 63 |  | %
Fan Type |  | EC Plug Fan
Voltage |  | 3 Ph 400 |  | V
Maximum Current Draw |  | 30 |  | A
Rated Power Consumption |  | 4.8 |  | kW
Return Filter Details
Pressure Drop |  | 45.5 |  | Pa
Filter Class |  | G4
Filter Dimensions |  | 1000x864x48 |  | mm
Quantity |  | 4 |  | pcs
Damper Details
Pressure Drop |  |  |  | Pa
Air Tightness Class |  | 3C
Damper Dimensions |  | 2350 x 900 |  | mm
Quantity |  | 1 |  | pcs
Project Name: | Enter your data
Unit: | Geniox Tera C Macro CRAH
Model: | TERA 170
Control and Electrical Configuration
Temperature & Humidity Sensor
Leak Detection
Water Valve
Corridor Sensor
Corridor Control
Power supply
Power Option & ATS
Power Measurement
User Terminal
Harmonic Filter
Panel Socket
Fire Protection
Communication Protocols for BMS
WSCO and Teamwork
Water Shut off valve

## Selection List
CAPACITY | 23 | 17: 170 Kw; 23: 230 kW; 30: 300 Kw
FLOW CONFIGURATION | F | B= TOP SIDE RETURN BOTTOM SUPPLY; F= TOP SIDE RETURN FRONT SUPPLY; M= FRONT SIDE RETURN BOTTOM SUPPLY
PIPE SIDE | R | L=Left; R=Right
WATER CONDITION | L | L= 20/28 ; H=20/30
HUMIDIFICATION | 0 | S= STEAM HUMIDIFIER 15kg/h ; 0= NONE
ESP | L | H= 100 Pa ESP; L= 50 Pa ESP ; S= …. Pa ESP
DAMPER | 1 | 1= ON TOP ; 0= NONE
Temp Sensors | O | S= Only Average Temp Sensor on Return/Supply Air; O= Additional Temp/Hum Sensor on Return/Supply Air
Leak Detaction | S | S= Wire Type ; O= Additional Leak Sensor
Valve Options | P | N= 0-10V Output w Temp Measurement; F= 0-10V Output w Flow/Temp Measurement; 3= 3 Way Valve; 2= 2 Way Valve w Temp Measurement; E= 2 Way Smart Energy Management Valve (EV) P= 2 Way Flow-Pressure Independent Valve (PICV)
Corridor Sensor | 0 | 0= None; 1= Corridors dP; 2= Double dP; 3= Corridor dP, Temperature & Humidity Sensor; 4= Double Corridor dP, Temperature & Humidity Sensor; 5=Temperature & Humidity Sensor
Corridor Control | 0 | 0: N/A; 1= Corridor Temperature Sensor is only for monitoring; 2= Corridor Temperature Sensor will be included on supply air
Power Input | 0 | 0= 400V /3P+N / 50hZ; 1= 400V / 3P+N / 60Hz
Power Option | B | N= None; A= ATS; B= ATS & UltraCap; U= UltraCap
Power Measurment | 3 | 0= None; 3= Energy Analyser
HMI | 2 | 0= None *; 1= Magnetic Text Based Display with Ethernet Socket Connection; 2= Panel Mounted Touch Panel Display
Harmonic Filter | 2 | 0= None ; 1= Active PFC ; 2= Fans with Active PFC
Panel Socket | A | 0= None; A=CF Type Socket
Fire Protection | 3 | N= None; 0= Shutdown on fire without sensor; 1= Continue on fire without sensor; 2= Shutdown with Smoke; 3= Continue with Smoke
Communication Protocols for BMS | 1 | 0=None; 1=BacNET IP; 2=BacNET MSTP; 3=Modbus RTU; 4=Modbus TCP/IP
WSCO and Teamwork | 1 | 0= None; 1=Teamwork; 2=WSCO**; 3=Teamwork and WSCO
Flow Direction | F | F : Supply from the front side; B : Bottom supply air to 3 sides ( front, left and right); A : All side
Safety Water Control Options | 0 | 0= None 0 : 1= Available
Unit Code = TERA C | 23FRL0L1OSP000B322A311F0 | * There will be no display at all. One text-based screen can be used in all units. If you choose none, please consider that you have to buy one text-based at least. ** If there is no electrical power measurement, WSCO will not be available.
47533.4017

## Sheet1 (hidden)
General Equipment | Product Number | Product Description | Amount | Unit | Unit Price | Total Price
Labor | HIZM000000010 | MONTAJ İŞÇİLİK OVERHEAD | 87.28 | pcs | 45 | 3927.6
| HIZM000000041 | ELEKTRİK ADAM SAAT | 18.77 | pcs | 45 | 844.65
| HIZM000000041 | ELEKTRİK ADAM SAAT Pano | 25.83 | pcs | 45 | 1162.35
CC Coil | R06TERAC00001 | 80T6R2P80NC Low Temp. | 0 | pcs | 3770 | 0
| R06TERAC00002 | 80T7R2P70NC High Temp. | 0 | pcs | 4305 | 0
| R06TERAC00003 | 84T7R2.3P147NC Low Temp. | 1 | pcs | 6680 | 6680
| R06TERAC00004 | 84T8R2.3P112NC High Temp. | 0 | pcs | 7410 | 0
| R06TERAC00005 | 82T7R2.3P143NC Low Temp. | 0 | pcs | 8050 | 0
| R06TERAC00006 | 82T8R2.3P112NC High Temp. | 0 | pcs | 9000 | 0
Fan | R05EBM0000284 | VBH0560CTTRS / EBM / 8300100101 | 0 | pcs | 812.4 | 0
| R058300100546 | EBM / 8300100546 | 4 | pcs | 958 | 3832
Nemlendirici | R13BN30150000 | BUHARLI NEMLENDIRICI EL 15KG/H | 0 | PCS | 1225 | 0
Electric Panel | R140023AR0003 | 1296x796x185 / Galvanized steel | 1 | pcs | 370 | 370
Air Filter | R170481000727 | PANEL FILTRE G4-48-1000x727 | 0 | pcs | 12.42 | 0
| R170481000672 | PANEL FILTRE G4-48-1000x672 | 8 | pcs | 11.74 | 93.92
| R17CF41000864 | 1028x864x48 G4 Panel Filtre | 0 | pcs | 50.68 | 0
| R170480525575 | PANEL FILTRE G4-48-525x725 | 0 | pcs | 7.96 | 0
| R170480905725 | PANEL FILTRE G4-48-905x725 | 0 | pcs | 11.51 | 0
Casing | R210090655150 | Corner 66x66 Top PA6-Steel Par | 4 | mt | 5.4 | 21.6
| R020090655021 | Corner profile 66x66 bottom | 8.5 | mt | 7.69 | 65.365
| R020090655020 | Corner profile 66x66 | 20.5 | mt | 7.59 | 155.595
| R020090653102 | MULLION 50X42 ZM310AC | 34.5 | mt | 5.31 | 183.195
| R020090653103 | 1/2 Mullion profile 25x42 ZM310AC | 17 | mt | 4 | 68
| R210090655073 | Mullion Bracket Top/Vertical | 6 | pcs | 0.45 | 2.7
| R210090655065 | Mullion Bracket 46,7x39,3x1,5 | 59 | pcs | 0.81 | 47.79
| R01B080000001 | 0.80 mm Z275 DX51 RAL7035 Boyalı Rulo Sac | 319.2 | kg | 1.07 | 341.544
| R040090655040 | Geniox panel profil tape/EPDM | 97.9 | mt | 3.1 | 303.49
| R040090655044 | Door profile w/tape + 1xTPE | 25.3 | mt | 2.44 | 61.732
| R01GL30000275 | 3.00 mm Z275 DX51 Plaka Sac | 241 | kg | 0.79 | 190.39
| R10YN60700002 | KAYA YÜNÜ 60MM-70 KG/M3 | 45 | m2 | 3.18 | 143.1
| R21KT50502520 | PUNTALI KAFES TELI (50mm X 50mm X2. 5mm)(1000x2000mm plakadan) | 0 | pcs | 51.12 | 0
| R21KT50502530 | PUNTALI KAFES TELI (50mm X 50mm X2. 5mm)(1000x3000mm plakadan) | 4 | pcs | 59.41 | 237.64
| R01BY27570400 | 1.2 MM 275 GR RAL7035 C.TARAF BOYALI SAC | 54 | kg | 1 | 54
| R01PS12000001 | 1.20 mm 316 Paslanmaz Nitto 9205 Pvc Kaplamalı Rulo Sac | 17.5 | kg | 4.22 | 73.85
| R210090655151 | Corner 25x66 Top PA6-Steel Par | 4 | pcs | 2.8 | 11.2
| R210090655153 | Corner 25x66 bot L PA6-Steel Par | 4 | pcs | 2.6 | 10.4
| R210090655154 | Corner 25x66 bot R PA6-Steel Par | 2 | pcs | 2.6 | 5.2
| R19KFL8155117 | 8-1551-17 Coverplate Lock Venthandle bluegrey | 12 | pcs | 5 | 60
| R1200000MKR40 | 40'lık Makaralı Ray (L=940 mm) | 8 | pcs | 16.44 | 131.52
| R21PD10010060 | 100x100x60 DELIKLI POLYAMID | 4 | pcs | 26 | 104
| R19KFLX2315F0 | KLIMA-FLEX ROD LINK 2651 - 902001 | 9 | pcs | 9.5 | 85.5
| R19KFLX081800 | 8mm Krom Kaplı İndüksiyonlu Mil (L=1800) | 3 | pcs | 3 | 9
| R190090655090 | L-Handle Non-locking K2-Grip | 3 | pcs | 1.32 | 3.96
| R190090655095 | K2 Adjustable Roller Cam | 9 | pcs | 0.96 | 8.64
| R190090655092 | K2 Latc Unit 60 mm | 9 | pcs | 1.79 | 16.11
| R210090655080 | Geniox Hinge Set | 15 | pcs | 1.74 | 26.1
| R210000238720 | HYGIENIC 110 w.foil grey 4,5x40 mm-20m/roll | 40 | mt | 0.54 | 21.6
| R210090655063 | 3D Clamp- Essentra | 8 | pcs | 1.43 | 11.44
| R01DK00000006 | 6.00 mm DKP sac | 5 | kg | 55 | 275
Piping | R21C300TERA01 | 4" Flanşlı dirsek | 2 | pcs | 155.7 | 311.4
| R21C300TERA04 | 4" Flanşlı dirsek / Çıkış | 1 | pcs | 261.39 | 261.39
| R21C300TERA02 | 4" Energy valve inlet pipe | 1 | pcs | 252 | 252
| R21FB43N00000 | 4" Flanşlı 3N boru | 0 | pcs | 248.68 | 0
| R21FB43N00000 | 4" Flanşlı 2 boru | 0 | pcs | 248.68 | 0
| R21FB43N00000 | 4" Flanşlı F boru | 0 | pcs | 248.68 | 0
| R21C300TERA03 | 4" Coil inlet pipe | 1 | pcs | 253.66 | 253.66
| R21FLNS400000 | 4" Flange | 2 | pcs | 11.33 | 22.66
| R21KORFLNS004 | 4" Blinde Flange | 2 | pcs | 10.09 | 20.18
| R21KLNGRT0004 | 4" Klingrit flanş contası | 8 | pcs | 1.12 | 8.96
| R21FLNS300000 | 3" Flanşlı dirsek | 0 | pcs | 127.93 | 0
| R21FDC3000000 | 3" Flanşlı dirsek / Çıkış | 0 | pcs | 184.3 | 0
| R21EVIP000003 | 3" Energy valve inlet pipe | 0 | pcs | 185.41 | 0
| R21FB43N00000 | 3" Flanşlı 3N boru | 0 | pcs | 248.68 | 0
| R21FB43N00000 | 3" Flanşlı 2 boru | 0 | pcs | 248.68 | 0
| R21FB43N00000 | 3" Flanşlı F boru | 0 | pcs | 248.68 | 0
| R21CIP0000003 | 3" Coil inlet pipe | 0 | pcs | 193.42 | 0
| R21FLNS300000 | 3" Flange | 0 | pcs | 127.93 | 0
| R21KORFLNS003 | 3" Blinde Flange | 0 | pcs | 15.83 | 0
| R21KLNGRT0003 | 3" Klingrit flanş contası | 0 | pcs | 0.8 | 0
| R16DIN9311680 | DIN 931 8.8 M16x80 PLAIN | 64 | pcs | 0.65 | 41.6
| R16DIN9348M16 | DIN 934 8 M16 PLAIN | 64 | pcs | 0.15 | 9.6
| R21SBK0000100 | 4" somunlu boru kelepçesi | 8 | pcs | 1.22 | 9.76
| R21SBK0000300 | 3" somunlu boru kelepçesi | 0 | pcs | 0.95 | 0
| R20PPRCDDR025 | PPRC 25mm Dış Dişli Rekor | 1 | pcs | 1.74 | 1.74
| R21DN20PPRC01 | DN20 PPRC İç Dişli Oynar Başlı Rakor | 1 | pcs | 1.85 | 1.85
| R20PPRCD25001 | DN20 PPRC 90 Derece Dirsek | 5 | pcs | 0.17 | 0.85
| R20PPRCB00025 | PPRC Boru 25 mm | 1 | mt | 0.87 | 0.87
| R21PN340000A1 | 3/4 " Pirinç Nipel | 1 | pcs | 0.88 | 0.88
| R2134PDDD2TID | 3/4 " Paslanmaz 90 Derece Dirsek 2 Tarafı İç Dişli | 1 | pcs | 3.65 | 3.65
| R2134PIDD2TID | 3/4 " Pirinç 90 Derece Dirsek 2 Tarafı İç Dişli | 1 | pcs | 2.63 | 2.63
| R21HK00001926 | 19-26 Hortum kelepçesi(3/4" hortum için) | 2 | pcs | 0.33 | 0.66
| R21SM0034CTSH | 3/4" Çelik telli spiral hortum | 1 | mt | 4.14 | 4.14
| R20PHL3400001 | Pirinç Hortum Lülesi 3/4" | 2 | pcs | 1.28 | 2.56
| R16AKB0M8X100 | M8X100 AKB Tam Diş 8.8 Kalite Civata | 50 | pcs | 0.15 | 7.5
Damper | R31TN17500900 | DAMPER TUNE AHU 1750(W) X 900(H) | 0 | pcs | 541 | 0
| R31TN13500900 | DAMPER TUNE AHU 1350(W) X 900(H) | 2 | pcs | 325 | 650
| R31TN23500900 | DAMPER TUNE AHU 2350(W) X 900(H) | 0 | pcs | 673 | 0
Cabling | R12QV50T45740 | QVT-CLICK 50-4 gy 45740 | 0 | pcs | 7.89 | 0
| R12QVT1645726 | QVT-CLICK 16 gy 45726 | 2 | pcs | 4.12 | 8.24
| R1200QTB42540 | Insert - QTB 42540 | 0 | pcs | 0.89 | 0
| R120QT1242512 | Insert - QT 12 42512 | 0 | pcs | 0.89 | 0
| R1200QT842508 | Insert - QT 8 42508 | 2 | pcs | 0.89 | 1.78
| R21KK15600047 | Kablo Bağı ve Ok Uçlu Montaj Klips 156-00047 | 200 | pcs |  | 0
| R12SAISK20290 | SAI-SK-M12UNI 2029 | 0 | pcs | 80 | 0
| R12SAISKBU000 | SAI-SK-M12 BU | 0 | pcs | 90 | 0
| R121058510150 | SAIL-M12GM12G-5S1.5U 1058510150 | 4 | pcs | 50.05 | 200.2
| R121058510300 | SAIL-M12GM12G-5S3.0U 1058510300 | 3 | pcs | 56 | 168
| R121058510500 | SAIL-M12GM12G-5S5.0U 1058510500 | 1 | pcs | 61.6 | 61.6
| R121058510100 | SAIL-M12GM12G-5S10U 1058511000 | 1 | pcs | 73.85 | 73.85
| R121353800000 | SAIE-M12B-5-0.2U P9 .75 1353800000 | 8 | pcs | 11.43 | 91.44
| R121783430000 | SAI-Y-5S PARA 2M12 1783430000 | 7 | pcs | 16.55 | 115.85
| R21OR0M20AP11 | M20AP11 M20 ERKEK-PG11 DISI PIRINC ADAPTOR ORTAC M20AP11 | 4 | pcs | 1.5 | 6
| R21OR0P11ROP9 | P11RP9 PG-11 ERKEK PG-9 DISI PIRINC REDUKSIYON ORTAC P11RP9 | 6 | pcs | 1 | 6
| R21OR0M16AP11 | M16AP11 M16 ERKEK-PG11 DISI PIRINC ADAPTOR ORTAC M16AP11 | 2 | pcs | 1.5 | 3
| R120700040057 | Adaptor M12 male / M12 male A-cod. 7000-40057-0000000 | 7 | pcs | 16.12 | 112.84
| R121807250000 | SAIB-5/9 (1807250000) | 1 | pcs | 96.25 | 96.25
| R21OR00M12AP9 | M12AP9 M12 ERKEK-PG9 DISI PIRINC ADAPTOR ORTAC M12AP9 | 2 | pcs | 1.3 | 2.6
| R121712630000 | HDC-KIT-HA 03.404 1712630000 | 5 | pcs | 15.79 | 78.95
| R121712570000 | HDC-KIT-HA 03.301 1712570000 | 1 | pcs | 20.74 | 20.74
Optional Control Equipment | R12NSX63A4P4D | Schneider ComPacT Şalter NSX100F 36kA AC 4P4D 63A | 1 | pcs | 75 | 75
| R12NSX80A4P4D | Schneider ComPacT Şalter NSX100F 36kA AC 4P4D 80A TMD | 0 | pcs | 90 | 0
| R12PGV2ME1600 | Schneider GV2ME16 Motor Koruma Şalteri 9-14A | 4 | pcs | 22 | 88
| R12PGVAE11000 | Schneider GVAE11 GV2 ve GV3P MKŞ YARDIMCI KONTAK 1NA + 1NK (ÖN MONTAJ) | 4 | pcs | 5 | 20
| R27AT93844006 | 4x63 A ATyS p M Haberlesmeli Otomatik Transfer (93844006) | 1 | pcs | 858.6 | 858.6
| R27AT93844008 | 4x80 A ATyS p M Haberlesmeli Otomatik Transfer (93844008) | 0 | pcs | 912.6 | 0
| R27TK22944016 | 4 Kutup için Üst ve Alt Terminal Kapagi (22944016) | 1 | pcs | 7.3 | 7.3
| R2740125AATYS | Tarak Tipi Köprüleme Barasi 40-125A ATyS M | 1 | pcs | 31.86 | 31.86
| R27AT95992020 | ATyS D20 (95992020) | 1 | pcs | 110 | 110
| R270007KT1661 | 7KT1661 Enerji Analizörü | 1 | pcs | 98.4 | 98.4
| R27AT100525VA | AL-CE ASB Serisi 125/5 – 15 VA – Baralı Tip – CL:0.5 Akım Trafosu | 3 | pcs | 53 | 159
| R27AHF50A400V | ABB Aktif Harmonik Filtre – Pqaktif | 0 | pcs | 3850 | 0
| R12PGV3P80300 | Schneider GV3P80 Motor Koruma Salteri GV3ME 56-80A | 0 | pcs | 150 | 0
| R12A9F746KA08 | Schneider A9F74110 iC60N 1x10A 6KA C OTOMAT | 1 | pcs | 3.5 | 3.5
| R27CAP24DC54K | QUINT4-CAP/24DC/5/4KJ - | 1 | pcs | 425 | 425
| R12A9F746KA08 | Schneider A9F74110 iC60N 1x10A 6KA C OTOMAT | 0 | pcs | 3.5 | 0
| R12KLM3071554 | Klemsan 670 300 PAP - UPS Ray Montajlı UPS Priz | 1 | pcs | 2 | 2
| R12A9F746KA07 | Schneider A9F74106 iC60N 1x6A 6KA C | 1 | pcs | 3 | 3
| R27PO95500709 | SIEMENS POL955.00/STD | 1 | pcs | 80.84 | 80.84
| R27POL0955515 | SIEMENS POL095.55/STD | 1 | pcs | 6.93 | 6.93
| R27ESSWAL05LM | IE-SW-AL05LM-5TX | 1 | pcs | 170 | 170
| R27POL8947235 | SIEMENS POL895.51/STD HMI | 0 | pcs | 124.49 | 0
| R27POL8T27070 | POL8T2.70/STD | 1 | pcs | 206.71 | 206.71
| R27POL0H85000 | POL0H8.50/STD Ekran Tutucu | 1 | pcs | 13.5 | 13.5
| R12KLM3071606 | Phoenix Contact 2987943 REL-MR- 24DC/21-21/MS | 1 | pcs | 3.68 | 3.68
| R12PHC298ECOR | Phoenix Contact 2907518 ECOR-1-BSC3/2X21 Röle tabanı | 1 | pcs | 2.1 | 2.1
| R12A9F7442000 | Schneider A9F74420 iK60N 4x20A 10KA C OTOMAT | 0 | pcs | 18.5 | 0
| R27QAM2120600 | QAM2120.600 -50...+80 °C, LG-Ni 1000, Duct temperature sensor 6000 mm | 2 | pcs | 83.16 | 166.32
| R24SAV6100001 | SAV61.00 Oransal vana motoru | 0 | pcs | 289 | 0
| R27VVF4310016 | VVF43.100-160 DN100 iki yollu vana gövdesi | 0 | pcs | 746 | 0
| R27VXF4310016 | VXF43.100-160 DN100 üç yollu vana gövdesi | 0 | pcs | 889.35 | 0
| R27VVF4380800 | VVF43.80-80 DN80 iki yollu vana gövdesi | 0 | pcs | 544 | 0
| R27VXF4380800 | VXF43.80-80 DN80 üç yollu vana gövdesi | 0 | pcs | 673 | 0
| R27FM080FSZ00 | FM080F-SZ Water Flow Meter DN80 | 0 | pcs | 352.77 | 0
| R27FM100FSZ00 | FM100F-SZ Water Flow Meter DN100 | 0 | pcs | 384.45 | 0
| R27EX080BAC00 | EV080F+BAC Energy Valve | 0 | pcs | 1933.14 | 0
| R27EV100FBAC0 | EV100F+BAC Energy Valve | 0 | pcs | 2243.34 | 0
| R27EP080FBAC0 | EP080F+MOD PICV Valve | 0 | pcs | 1657.26 | 0
| R270EP100FMOD | EP100F+MOD PICV Valve | 1 | pcs | 1937.43 | 1937.43
| R27DN80161433 | DN80 Flange Shut-Off Valve / PN16 / Ayvaz (1433) | 0 | pcs | 449.1 | 0
| R27DN10161433 | DN100 Flange Shut-Off Valve / PN16 / Ayvaz (1433) | 0 | pcs | 477.16 | 0
| R24QAE2120011 | QAE2120.010 | 0 | pcs | 45.75 | 0
| R27ALTSS00100 | ALT-SS100 Protection pocket, 100 mm | 0 | pcs | 11.1 | 0
| R24QBM20301U0 | QBM2030-1U QBM2030-1U Diff. pressure sensor | 0 | pcs | 65.4 | 0
| R24QFA3160001 | QFA3160 Room sensor for humidity (DC 0...10 V) and temperature (DC 0...10 V) | 0 | pcs | 130.41 | 0
| R27DAGCA1211E | GCA121.1E Damper Motoru | 2 | pcs | 106.6 | 213.2
| R27QFM2150MO6 | QFM2150/MO -40…70 ℃, AC/DC 24 V, Modbus RTU | 2 | pcs | 44.82 | 89.64
| R27QBM2700022 | QBM9777/109C Air differential pressure sensor, Modbus RTU, IP54, 2x AI (LG-Ni1000, Pt1000, NTC 10k, DC 0...10 V), 2x AO (DC 0...10 V), 2 x 7000 Pa, multipack 20 pcs. | 1 | pcs | 83.54 | 83.54
| R27QBM1100022 | QBM9711/109C Air differential pressure sensor, Modbus RTU, IP54, 2x AI (LG-Ni1000, Pt1000, NTC 10k, DC 0...10 V), 2x AO (DC 0...10 V), 2 x 1250 Pa, | 1 | pcs | 83.54 | 83.54
| R270302240501 | FLOR000000 Water leak sensor stripe type | 10 | mt | 19.207 | 192.07
| R27FLS9785266 | FLOS000000 Water leak sensor spote type | 0 | pcs | 19.33 | 0
| R27SDSFFS0000 | CAREL SFFS000000 Smoke Detector | 1 | pcs | 315.75 | 315.75
standart panel | R120LV429338T | SCHNEIDER LV429338T UZATMALI DÖNER KURMA KOL | 1 | pcs | 20 | 20
| R12PXC01A5X20 | Siba 179120.1 Sigortalı Klemensler için Minyatur Cam Sigorta - 1 A (5x20) | 3 | pcs | 0.1 | 0.3
| R27MKC0000006 | ENTES MKC-01 FAZ KORUMA ROLESI | 1 | pcs | 20 | 20
| R12PA9D346250 | Schneider A9D34625 iDPNa 1P+N C Type 30mA 25A KAÇAK AKIMLI SİGORTA | 1 | pcs | 26 | 26
| R12A9F746KA05 | Schneider A9F74102 iC60N 1x2A 6KA C OTOMAT | 1 | pcs | 4 | 4
| R12KLM3071603 | DELTA DRL-24V240W1A 24VDC 10A GUC KAYNAGI | 1 | pcs | 34.2 | 34.2
| R12A9F746KA07 | Schneider A9F74106 iC60N 1x6A 6KA C | 1 | pcs | 3 | 3
| R12KS40000000 | KAPI SWİTCHİ (XCKP2145P16) | 1 | pcs | 19 | 19
| R12EPL2509740 | MOMENTUM EPL25097 LED PANEL LIGHTNING 220V 40CM | 1 | pcs | 8 | 8
| R12PXC02A5X20 | Siba 179120.2 Sigortalı Klemensler için Minyatur Cam Sigorta - 2 A (5x20) | 1 | pcs | 0.1 | 0.1
| R12PXC3211861 | Phoenix Contact 3211861 PT 4-HESI (5X20) SİGORTALI KLEMENS | 3 | pcs | 2.8 | 8.4
| R27POL64810S7 | POL648.10/STD | 1 | pcs | 213.22 | 213.22
| R27POL6486001 | POL064.86/STD Terminal Set | 1 | pcs | 11.39 | 11.39
| R12GW4X11125A | GW-4x11 4 Kutuplu 1x10mm2 125A Girişli Dağıtıcı Ünite | 1 | pcs | 10 | 10
| R12SBRJ45RS45 | Ethernet Socket BRJ45 Ethernet | 1 | pcs | 10 | 10
| R12PXC3209510 | Phoenix Contact 3209510 PT 2,5 Yay Baskılı 1G1Ç Klemens Gri | 34 | pcs | 0.4 | 13.6
| R12PXC3209536 | Phoenix Contact 3209536 PT 2,5-PE Yay Baskılı 1G1Ç Klemens Toprak | 5 | pcs | 1.5 | 7.5
| R12PMIT150021 | Molwex PMIT15 6-6x2,5 Pushin, 6x2,5 mm2 Dağıtıcı Blok | 2 | pcs | 3 | 6
| R12KLM3071630 | TORK APTK-80A10 10 DELİKLİ TOPRAK KLEMENSİ | 1 | pcs | 2 | 2
| R12KLM3071566 | Klemsan 555 2580 KKD 2580 Delikli kablo kanalı Gri (28x2 m) | 1 | mt | 2 | 2
| R12KLM3071569 | Klemsan 555 4080 KKD 4080 Delikli kablo kanalı Gri (20x2 m) | 2 | mt | 2.5 | 5
| R12KLM3071572 | Klemsan 555 6080 KKD 6080 Delikli kablo kanalı Gri (12x2 m) | 1 | mt | 3 | 3
| R12KLM3071553 | Klemsan 501 101 RT Ray Yükseltici | 2 | pcs | 0.36 | 0.72
| R12KLM2062005 | Klemsan 500 604 MR 35 35 x 7,5 MONTAJ RAYI (2mt) | 2 | mt | 4 | 8
| R123476A042AB | CANON TE 3467B 001AA Yazıcı kartuşu siyah renk (100mt) çipli | 1 | pcs | 18 | 18
| R123476M280YA | CANON TE 3476M 200YA Sarı çap 2.0mm ISI İLE DARALAN MARKALAMA MAKARONLARI | 1 | mt | 0.13 | 0.13
| R123476M400YA | CANON TE 3476M 320YA Sarı çap 3.2mm ISI İLE DARALAN MARKALAMA MAKARONLARI | 1 | mt | 0.18 | 0.18
| R12UY3005S002 | ŞAFAK UY-3007S 1x0.75mm2 MAVİ YÜKSÜK | 4 | pcs | 0.01 | 0.04
| R12UY3005S003 | ŞAFAK UY-3010S 1x1mm2 KIRMIZI YÜKSÜK | 150 | pcs | 0.01 | 1.5
| R12UY3005S005 | ŞAFAK UY-3025S 1x2,5mm2 GRİ YÜKSÜK | 10 | pcs | 0.01 | 0.1
| R12UY3005S012 | ŞAFAK UY-23010S 2x1mm2 KIRMIZI YÜKSÜK | 20 | pcs | 0.01 | 0.2
| R12UY3005S014 | ŞAFAK UY-23025S 2x2,5mm2 GRİ YÜKSÜK | 6 | pcs | 0.05 | 0.3
| R12H05Z100100 | 1x1mm2 H05Z1-K KABLO KAHVERENGİ | 15 | mt | 0.2 | 3
| R12H05Z100111 | 1x1mm2 H05Z1-K KABLO SİYAH | 6 | mt | 0.2 | 1.2
| R12H05Z100114 | 1x1mm2 H05Z1-K KABLO BEYAZ | 15 | mt | 0.2 | 3
| R12H05Z100115 | 1x1mm2 H05Z1-K KABLO YEŞİL | 60 | mt | 0.2 | 12
| R12H05Z100116 | 1x1mm2 H05Z1-K KABLO MAVİ | 10 | mt | 0.2 | 2
| R12H05Z100117 | 1x1mm2 H05Z1-K KABLO SARI YEŞİL | 2 | mt | 0.2 | 0.4
| R12H05Z150115 | 1x2,5mm2 H05Z1-K KABLO SİYAH | 2 | mt | 0.35 | 0.7
| R12H05Z150118 | 1x2,5mm2 H05Z1-K KABLO SARI YEŞİL | 2 | mt | 0.35 | 0.7
| R12KBLIHCH2X0 | LIHCH 2X0,75MM2 KABLO | 1 | mt | 0.39 | 0.39
| R12PXC3030417 | Phoenix Contact 3030417 D-ST 2,5 Nihayet Plakası | 5 | pcs | 0.3 | 1.5
| R12P302227635 | Phoenix Contact 3022276 CLIPFIX 35-5 Vidasız Durdurucu | 10 | pcs | 0.45 | 4.5
| R12TBYK30563P | ONKA 3056 3P Tarak Baralar Için YAN KAPAK | 2 | pcs | 0.4 | 0.8
| R12PXC0811969 | Phoenix Contact 811969 KLM 3 Grup Etiketliği | 1 | pcs | 0.3 | 0.3
| R27CR2032SP01 | VARTA CR2032 PLC ZAMAN SAATI PILI | 1 | pcs | 1 | 1
| R12PXC0828734 | Phoenix Contact 828734 UCT-TM 5 - Klemens Etiketi | 3 | pcs | 2.75 | 8.25
| R12P303021335 | Phoenix Contact 3030213 FBS 10-5 Geçme Tip Üst Köprü | 6 | pcs | 1.6 | 9.6
| R12BGK1140013 | ONKA 1140013 No1 (2.5-10mm2) Tarak Bara Güç Klemensi | 5 | pcs | 0.56 | 2.8
| R12PXC0828736 | Phoenix Contact 828736 UCT-TM 6 - Klemens Etiketi | 1 | pcs | 2.1 | 2.1
| R12PXC3211757 | Phoenix Contact 3211757 PT 4 Yay Baskılı 1G1Ç Klemens Gri | 3 | pcs | 0.55 | 1.65
| R12PXC3211760 | Phoenix Contact 3211760 PT 4 BU Yay Baskılı 1G1Ç Klemens Mavi | 1 | pcs | 0.55 | 0.55
| R12PXC3211766 | Phoenix Contact 3211766 PT 4-PE Yay Baskılı 1G1Ç Klemens Toprak | 1 | pcs | 1.75 | 1.75
| R12NCAT600002 | Cat6 Patch Kablo 2 Metre | 1 | pcs | 3 | 3
|  | TOTAL |  |  | 28520.041

## Sayfa2 (hidden)
| 17 | 170
| 23 | 230
| 30 | 300
FLOW CONFIGURATION | B | #NAME?
| F | #NAME?
| M | #NAME?
PIPE SIDE | L | #NAME?
| R | #NAME?
WATER CONDITION | L | 0.71429
| H | 0.66667
HUMIDIFICATION | S | = STEAM HUMIDIFIER 15kg/h
| 0 | #NAME?
ESP | H | = 100 Pa ESP
| L | = 50 Pa ESP
| S | #NAME?
DAMPER | 1 | #NAME?
| 0 | #NAME?
Temp Sensors | S | #NAME?
| O | #NAME?
Leak Detaction | S | #NAME?
| O | #NAME?
Valve Options | N | = Only 0-10V Cooling Demand output
| F | = Flowmeter and 0-10V Output
| 2 | = 2 Way Valve
| 3 | = 3 Way Valve (Valve possitioned out of the unit at the pipe outlet, bypass line should be done by customer)
| E | = 2 Way Valve w Energy Measurement
| P | #NAME?
Corridor Control | 0 | #NAME?
| 1 | #NAME?
| 2 | #NAME?
| 3 | = Corridors dP and Temperature Sensor***
| 4 | = Corridors Double dP and Temperature Sensor***
| 5 | =Temperature Sensor ***
Power | 0 | = 400V /3P+N / 50hZ
| 1 | = 400V / 3P+N / 60Hz
Power Supply | N | #NAME?
A
B
| U | #NAME?
Power Measurment | 0 | #NAME?
| 3 | #NAME?
HMI | 0 | = None *
| 1 | = On Control Panel (Text-Based)
| 2 | #NAME?
Harmonic Filter | 0 | = None **
1
| 2 | #NAME?
Panel Socket | 0 | #NAME?
| A | #NAME?
Fire Protection | N | #NAME?
| 0 | #NAME?
| 1 | #NAME?
| 2 | #NAME?
| 3 | #NAME?
Communication Protocols for BMS | 0 | #NAME?
| 1 | #NAME?
| 2 | #NAME?
| 3 | #NAME?
| 4 | #NAME?
WSCO and Teamwork | 0 | #NAME?
| 1 | #NAME?
| 2 | #NAME?
| 3 | #NAME?
Flow Direction | F | : Supply from the front side
| B | : Bottom supply air to 3 sides ( front, left and right)
| A | : All side
Safety Water Control Options | 0 | : Shut Of Valve
| 1 | : None
0
Corridor Control | 1 | 1= Corridor Temperature Sensor is only for monitoring
| 2 | 2= Corridor Temperature Sensor will be included on supply air
Note on A16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Available for B and F Flow Configuration
Note on A22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Ahmet Murat Tunç @Nadide Asuman Yaraş I see that in systemp selection we can also add 3 way valve. Maybe we can leave this option but mark that it is to be installed outside the unit? Reply: @Anna Kondratenko added Reply: @Ahmet Murat Tunç thank you
Note on A28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Ahmet Murat Tunç @Nadide Asuman Yaraş please add here option for extra temperature sensors Reply: @Anna Kondratenko done
Note on A36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Ahmet Murat Tunç in some cases there is requirement for no neutral power supply. Can we provide such option off the shelve? Reply: @Anna Kondratenko If we add no neutral option, it will not be possible to add extra equipment's to the control panel on full option. I prefer to keep it as special requirement. As you know customer will not ask for full option %99 but it will be a risk for no reason. Also in Rennes, when we talked with customer, they were OK to give neutral. So, it wasn't really a requirement from customer side, they were also surprised when they saw the unit. They asked for neutral connection on FAT. Reply: Addition to the SEmih when we choose without N, panel depth and dminesion is not enough. Reply: @Ahmet Murat Tunç @Semih Uyar ok, then we take it as special requirement
Note on B42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Ahmet Murat Tunç @Nadide Asuman Yaraş please clarify here> one user terminal will be common for group of XX units Reply: @Anna Kondratenko done
Note on B43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Nadide Asuman Yaraş @Ahmet Murat Tunç please clarify here that it will be text base Reply: @Anna Kondratenko done.
Note on B45: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Ahmet Murat Tunç @Nadide Asuman Yaraş add clarification regarding fans with passive harmonic filters on default Reply: @Anna Kondratenko done
Note on A55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Ahmet Murat Tunç @Nadide Asuman Yaraş add communicational protocols Reply: @Anna Kondratenko done
Note on A64: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Serhan Tayfun Arslan please clarify here it is air supply. Reply: @Serhan Tayfun Arslan what do you mean with all side? I would put next> F - for frontal, B - bottom supply air to 3 sides in the false floor Reply: @Anna Kondratenko By all side I mean airflow from all sides. I corrected F and B option.