## Template3
Project Name: | Enter your data
Unit: | Geniox Tera C Macro CRAH
Model: | TERA 170
Unit summary |  |  | Version 1.1.0.0
Configuration |  |  | TOP RETURN BOTTOM SUPPLY
Cooling capacity |  |  | 340.7
Airflow |  |  | 33333
Supply/Return air temperature |  |  | 14.2/44
Power supply |  |  | 400V-3PH-N-PE-50Hz
Dimensions (W x L x H) |  |  | 4082 x 1082 x 3200 mm
Casing/Frame Details
Panel Thickness |  |  | 60 mm
Panel Insulation Type / Density |  |  | Rock wool 60kg/m3
Panel External Sheet |  |  | Z275 Steel + Polyster Painted (0,80mm)
Panel Internal Sheet |  |  | Z275 Steel + Polyster Painted (0,80mm)
Frame Type |  |  | Z275 + Epoxy Primer Polyester Painted Steel
Water Cooling Coil Details
Fluid |  | WATER |  | %
Return Air Temparature |  | 44 |  | °C
Return Air Humidity |  | 11 |  | %
Supply Air Temparature |  | 14.2 |  | °C
Supply Air Humidity |  | 62.2 |  | %
Coil Pressure Drop (Air side) |  | 102.8 |  | Pa
Coil Cooling Capacity |  | 340.7 |  | kW
Fluid Inlet Temparature. |  | 11 |  | °C
Fluid Outlet Temparature |  | 22 |  | °C
Water Flow Rate |  | 26.6 |  | m³/h
Coil Pressure Drop (Fluid side) |  | 85.8 |  | kPa
EER (Energy Efficiency Ratio) |  | 71
Connections (Inlet-Outlet) |  | DN 80
Air density |  |  |  | kg/m³
Supply Fan Details
Air Flow Rate |  | 33333 |  | m³/h
External Pressure |  | 111 |  | Pa
Total Static Pressure |  | 259.3 |  | Pa
Fan Speed |  | 1513 |  | rpm
Maximum Fan Speed |  | 2370 |  | rpm
Total Efficiency |  | 63 |  | %
Fan Type |  | EC Plug Fan
Voltage |  | 3 Ph 400 |  | V
Maximum Current Draw |  | 30 |  | A
Rated Power Consumption |  | 4.8 |  | kW
Return Filter Details
Pressure Drop |  | 45.5 |  | Pa
Filter Class |  | G4
Filter Dimensions |  | 1000x864x48 |  | mm
Quantity |  | 4 |  | pcs
Damper Details
Pressure Drop |  |  |  | Pa
Air Tightness Class |  | 3C
Damper Dimensions |  | 2350 x 900 |  | mm
Quantity |  | 1 |  | pcs

## Selection List (hidden)
CAPACITY | 17 | 15: 150 kW; 17: 170 Kw; 23: 230 kW; 30: 300 Kw
FLOW CONFIGURATION | B | B= TOP SIDE RETURN BOTTOM SUPPLY; F= TOP SIDE RETURN FRONT SUPPLY; M= FRONT SIDE RETURN BOTTOM SUPPLY
PIPE SIDE | R | L=Left; R=Right
WATER CONDITION | H | -5371
HUMIDIFICATION | S | S= STEAM HUMIDIFIER 15kg/h ; 0= NONE
ESP | H | H= 100 Pa ESP; L= 50 Pa ESP ; S= …. Pa ESP
DAMPER | 0 | 1= ON TOP ; 0= NONE
Temp Sensors | S | S= Only Average Temp Sensor on Return/Supply Air; O= Additional Temp/Hum Sensor on Return/Supply Air
Leak Detaction | S | S= Wire Type ; O= Additional Leak Sensor
Valve Options | N | N= 0-10V Output w Temp Measurement; F= 0-10V Output w Flow/Temp Measurement; 3= 3 Way Valve; 2= 2 Way Valve w Temp Measurement; E= 2 Way Smart Energy Management Valve (EV) P= 2 Way Flow-Pressure Independent Valve (PICV)
Corridor Sensor | 0 | 0= None; 1= Corridors dP; 2= Double dP; 3= Corridor dP, Temperature & Humidity Sensor; 4= Double Corridor dP, Temperature & Humidity Sensor; 5=Temperature & Humidity Sensor
Corridor Control | 0 | 0: N/A; 1= Corridor Temperature Sensor is only for monitoring; 2= Corridor Temperature Sensor will be included on supply air
Power Input | 0 | 0= 400V /3P+N / 50hZ; 1= 400V / 3P+N / 60Hz
Power Option | N | N= None; A= ATS; B= ATS & UltraCap; U= UltraCap
Power Measurment | 0 | 0= None; 3= Energy Analyser
HMI | 0 | 0= None *; 1= Magnetic Text Based Display with Ethernet Socket Connection; 2= Panel Mounted Touch Panel Display
Harmonic Filter | 0 | 0= None **; 1= Active PFC
Panel Socket | 0 | 0= None; A=CF Type Socket
Fire Protection | N | N= None; 0= Shutdown on fire without sensor; 1= Continue on fire without sensor; 2= Shutdown with Smoke; 3= Continue with Smoke
Communication Protocols for BMS | 0 | 0=None; 1=BacNET IP; 2=BacNET MSTP; 3=Modbus RTU; 4=Modbus TCP/IP
WSCO and Teamwork | 0 | 0= None; 1=Teamwork; 2=WSCO***; 3=Teamwork and WSCO
Flow Direction | F | F : Supply from the front side; B : Bottom supply air to 3 sides ( front, left and right); A : All side
Safety Water Control Options | 0 | 0= None 0 : 1= Available
Unit Code = TERA C | 17BRHSH0SSN000N0000N00F0 | * * There will be no display at all. One text-based screen can be used in all units. If you choose none, please consider that you have to buy one text-based at least. ** ** Please consider that all fans have its own passive harmonic filter ***If there is no electrical power measurement, WSCO will not be available.
TOTAL COST | 27875.8443

## Calculation (hidden)
CAPACITY | 24016.9
FLOW CONFIGURATION | 1457.95
PIPE SIDE | 0
WATER CONDITION | 759
HUMIDIFICATION | 1363.7833
ESP | 0
DAMPER | 0
Temp Sensors | 3.7423
Leak Detaction | 0
Valve Options | 120.8712
Corridor Sensor | 0
Corridor Control | 0
Power Input | 0
Power Option | 0
Power Measurment | 0
HMI | 0
Harmonic Filter | 0
Panel Socket | 0
Fire Protection | 0
Communication Protocols for BMS | 0
WSCO and Teamwork | 0
Flow Direction | 0
Safety Water Control Options | 0
PLC Ext. Module | 153.5975
TOTAL | 27875.8443

## Sayfa2 (hidden)
CAPACITY¹ | 15 | 150
| 17 | 170
| 23 | 230
| 30 | 300
FLOW CONFIGURATION | B | #NAME?
| F | #NAME?
| M | #NAME?
PIPE SIDE | L | #NAME?
| R | #NAME?
WATER CONDITION | L | 0.71429
| H | 0.66667
HUMIDIFICATION | S | = STEAM HUMIDIFIER 15kg/h
| 0 | #NAME?
ESP | H | = 100 Pa ESP
| L | = 50 Pa ESP
| S | #NAME?
DAMPER | 1 | #NAME?
| 0 | #NAME?
Temp Sensors | S | #NAME?
| O | #NAME?
Leak Detaction | S | #NAME?
| O | #NAME?
Valve Options | N | = Only 0-10V Cooling Demand output
| F | = Flowmeter and 0-10V Output
| 2 | = 2 Way Valve
| 3 | = 3 Way Valve (Valve possitioned out of the unit at the pipe outlet, bypass line should be done by customer)
| E | = 2 Way Valve w Energy Measurement
| P | #NAME?
Corridor Control | 0 | #NAME?
| 1 | #NAME?
| 2 | #NAME?
| 3 | = Corridors dP and Temperature Sensor***
| 4 | = Corridors Double dP and Temperature Sensor***
| 5 | =Temperature Sensor ***
Power | 0 | = 400V /3P+N / 50hZ
| 1 | = 400V / 3P+N / 60Hz
Power Supply | N | #NAME?
A
B
| U | #NAME?
Power Measurment | 0 | #NAME?
| 3 | #NAME?
HMI | 0 | = None *
| 1 | = On Control Panel (Text-Based)
| 2 | #NAME?
Harmonic Filter | 0 | = None **
| 1 | #NAME?
Panel Socket | 0 | #NAME?
| A | #NAME?
Fire Protection | N | #NAME?
| 0 | #NAME?
| 1 | #NAME?
| 2 | #NAME?
| 3 | #NAME?
Communication Protocols for BMS | 0 | #NAME?
| 1 | #NAME?
| 2 | #NAME?
| 3 | #NAME?
| 4 | #NAME?
WSCO and Teamwork | 0 | #NAME?
| 1 | #NAME?
| 2 | #NAME?
| 3 | #NAME?
Flow Direction | F | : Supply from the front side
| B | : Bottom supply air to 3 sides ( front, left and right)
| A | : All side
Safety Water Control Options | 0 | : Shut Of Valve
| 1 | : None
0
Corridor Control | 1 | 1= Corridor Temperature Sensor is only for monitoring
| 2 | 2= Corridor Temperature Sensor will be included on supply air
Note on A17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Available for B and F Flow Configuration
Note on A23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Ahmet Murat Tunç @Nadide Asuman Yaraş I see that in systemp selection we can also add 3 way valve. Maybe we can leave this option but mark that it is to be installed outside the unit? Reply: @Anna Kondratenko added Reply: @Ahmet Murat Tunç thank you
Note on A29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Ahmet Murat Tunç @Nadide Asuman Yaraş please add here option for extra temperature sensors Reply: @Anna Kondratenko done
Note on A37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Ahmet Murat Tunç in some cases there is requirement for no neutral power supply. Can we provide such option off the shelve? Reply: @Anna Kondratenko If we add no neutral option, it will not be possible to add extra equipment's to the control panel on full option. I prefer to keep it as special requirement. As you know customer will not ask for full option %99 but it will be a risk for no reason. Also in Rennes, when we talked with customer, they were OK to give neutral. So, it wasn't really a requirement from customer side, they were also surprised when they saw the unit. They asked for neutral connection on FAT. Reply: Addition to the SEmih when we choose without N, panel depth and dminesion is not enough. Reply: @Ahmet Murat Tunç @Semih Uyar ok, then we take it as special requirement
Note on B43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Ahmet Murat Tunç @Nadide Asuman Yaraş please clarify here> one user terminal will be common for group of XX units Reply: @Anna Kondratenko done
Note on B44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Nadide Asuman Yaraş @Ahmet Murat Tunç please clarify here that it will be text base Reply: @Anna Kondratenko done.
Note on B46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Ahmet Murat Tunç @Nadide Asuman Yaraş add clarification regarding fans with passive harmonic filters on default Reply: @Anna Kondratenko done
Note on A55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Ahmet Murat Tunç @Nadide Asuman Yaraş add communicational protocols Reply: @Anna Kondratenko done
Note on A64: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Serhan Tayfun Arslan please clarify here it is air supply. Reply: @Serhan Tayfun Arslan what do you mean with all side? I would put next> F - for frontal, B - bottom supply air to 3 sides in the false floor Reply: @Anna Kondratenko By all side I mean airflow from all sides. I corrected F and B option.

## Material Costs (hidden)
|  | 170 | 230 | 300 | 170 | 230 | 300
CAPACITY | 17=170 | 14440.1544 | 20956.5818 | 24574.7071 | 24016.9 | 35008.94 | 41208.74
| 23=230 | 0 | 0 | 0 | 0 | 0 | 0
| 30=300 | 0 | 0 | 0 | 0 | 0 | 0
FLOW CONFIGURATION | B= TOP SIDE RETURN BOTTOM SUPPLY | 874.77 | 1046.065 | 1198.6175 | 1457.95 | 1743.4417 | 1997.6958
| F= TOP SIDE RETURN FRONT SUPPLY | 713.4175 | 878.8325 | 1037.265 | 1189.0292 | 1464.7208 | 1728.775
| M= FRONT SIDE RETURN BOTTOM SUPPLY | 921.53 | 1103.1925 | 1270.745 | 1535.8833 | 1838.6542 | 2117.9083
PIPE SIDE | L=Left | 0 | 0 | 0 | 0 | 0 | 0
| R=Right | 0 | 0 | 0 | 0 | 0 | 0
WATER CONDITION | L= 20/28 | 0 | 0 | 0 | 0 | 0 | 0
| H=20/30 | 455.4 | 589.05 | 773.85 | 759 | 981.75 | 1289.75
HUMIDIFICATION | S= STEAM HUMIDIFIER 15kg/h | 818.27 | 818.27 | 818.27 | 1363.7833 | 1363.7833 | 1363.7833
| 0= NONE | 0 | 0 | 0 | 0 | 0 | 0
ESP | H= 100 Pa ESP | 0 | 0 | 0 | 0 | 0 | 0
| L= 50 Pa ESP | 0 | 0 | 0 | 0 | 0 | 0
| S= …. Pa ESP | 0 | 0 | 0 | 0 | 0 | 0
DAMPER | 1= ON TOP | 897.511 | 874.511 | 1306.511 | 1495.8517 | 1457.5183 | 2177.5183
| 0= NONE | 0 | 0 | 0 | 0 | 0 | 0
Return/Supply Temp/Hum Sensors | S= Only Average Temp Sensor on Return/Supply Air | 2.2454 | 2.2454 | 2.2454 | 3.7423 | 3.7423 | 3.7423
| O= Additional Temp/Hum Sensor on Return/Supply Air | 255.1168 | 255.1168 | 255.1168 | 425.1947 | 425.1947 | 425.1947
Leak Detection | S= Wire Type Water Leak Sensor | 0 | 0 | 0 | 0 | 0 | 0
| O= Additional Wire Type Water Leak Sensor | 192.0765 | 192.0765 | 192.0765 | 320.1275 | 320.1275 | 320.1275
Valve Options | N= 0-10V Output w Temp Measurement | 72.5227 | 72.5227 | 72.5227 | 120.8712 | 120.8712 | 120.8712
| F= 0-10V Output w Flow/Temp Measurement | 577.2227 | 627.2027 | 652.2027 | 962.0378 | 1045.3378 | 1087.0045
| 2= 2 Way Valve w Temp Measurement | 1115.0537 | 1024.3862 | 1049.3862 | 1858.4228 | 1707.3103 | 1748.977
| 3= 3 Way Valve w Temp Measurement (Valve positioned out of the unit at the pipe outlet, bypass line should be done by customer) | 1250.5037 | 1477.6712 | 1502.6712 | 2084.1728 | 2462.7853 | 2504.452
| E= 2 Way Smart Energy Management Valve (EV) | 1978.48 | 2267.86 | 2292.86 | 3297.4667 | 3779.7667 | 3821.4333
| P= 2 Way Flow-Pressure Independent Valve (PICV) | 1721.125 | 1982.68 | 2007.68 | 2868.5417 | 3304.4667 | 3346.1333
Corridor Sensor | 0= None | 0 | 0 | 0 | 0 | 0 | 0
| 1= Corridor dP | 68.712 | 68.712 | 68.712 | 114.52 | 114.52 | 114.52
| 2= Double Corridor dP | 137.424 | 137.424 | 137.424 | 229.04 | 229.04 | 229.04
| 3= Corridor dP, Temperature & Humidity Sensor | 213.339 | 213.339 | 213.339 | 355.565 | 355.565 | 355.565
| 4= Double Corridor dP, Temperature & Humidity Sensor | 282.051 | 282.051 | 282.051 | 470.085 | 470.085 | 470.085
| 5=Temperature & Humidity Sensor | 144.627 | 144.627 | 144.627 | 241.045 | 241.045 | 241.045
Corridor Control | 0= N/A | 0 | 0 | 0 | 0 | 0 | 0
| 1= Corridor Temperature Sensor is only for monitoring | 0 | 0 | 0 | 0 | 0 | 0
| 2= Corridor Temperature Sensor will be included on supply air | 0 | 0 | 0 | 0 | 0 | 0
Power Input | 0= 400V / 3P+N / 50 Hz | 0 | 0 | 0 | 0 | 0 | 0
| 1= 400V / 3P+N / 60 Hz | 0 | 0 | 0 | 0 | 0 | 0
Power Option & ATS | N= None | 0 | 0 | 0 | 0 | 0 | 0
| A= ATS | 1069.047 | 1069.047 | 1069.047 | 1781.745 | 1781.745 | 1781.745
| B= ATS & UltraCap | 1484.7218 | 1484.7218 | 1484.7218 | 2474.5364 | 2474.5364 | 2474.5364
| U= UltraCap | 415.6748 | 415.6748 | 415.6748 | 692.7914 | 692.7914 | 692.7914
Power Measurment | 0= None | 0 | 0 | 0 | 0 | 0 | 0
| 3= Energy Analyser | 316.05 | 316.05 | 316.05 | 526.75 | 526.75 | 526.75
HMI | 0= None * | 0 | 0 | 0 | 0 | 0 | 0
| 1= Magnetic Text Based Display with Ethernet Socket Connection | 114.66 | 114.66 | 114.66 | 191.1 | 191.1 | 191.1
| 2= Panel Mounted Touch Panel Display | 294.2423 | 294.2423 | 294.2423 | 490.4038 | 490.4038 | 490.4038
Harmonic Filter | 0= None ** | 0 | 0 | 0 | 0 | 0 | 0
| 1= Active PFC | 6431.4715 | 6431.4715 | 6431.4715 | 10719.1192 | 10719.1192 | 10719.1192
| 2= Fans with Active PFC | 436.8 | 582.4 | 728 | 728 | 970.6667 | 1213.3333
Panel Socket | 0= None | 0 | 0 | 0 | 0 | 0 | 0
| A=CF Type Socket | 4.9039 | 4.9039 | 4.9039 | 8.1732 | 8.1732 | 8.1732
Fire Protection | N= None | 0 | 0 | 0 | 0 | 0 | 0
| 0= Shutdown on fire without sensor | 6.0585 | 6.0585 | 6.0585 | 10.0975 | 10.0975 | 10.0975
| 1= Continue on fire without sensor | 6.0585 | 6.0585 | 6.0585 | 10.0975 | 10.0975 | 10.0975
| 2= Shutdown with Smoke | 236.5028 | 236.5028 | 236.5028 | 394.1713 | 394.1713 | 394.1713
| 3= Continue with Smoke | 236.5028 | 236.5028 | 236.5028 | 394.1713 | 394.1713 | 394.1713
Communication Protocols for BMS | 0=None | 0 | 0 | 0 | 0 | 0 | 0
| 1=BacNET IP | 0 | 0 | 0 | 0 | 0 | 0
| 2=BacNET MSTP | 0 | 0 | 0 | 0 | 0 | 0
| 3=Modbus RTU | 0 | 0 | 0 | 0 | 0 | 0
| 4=Modbus TCP/IP | 0 | 0 | 0 | 0 | 0 | 0
WSCO and Teamwork | 0= None | 0 | 0 | 0 | 0 | 0 | 0
| 1=Teamwork | 189 | 189 | 189 | 315 | 315 | 315
| 2=WSCO*** | 0 | 0 | 0 | 0 | 0 | 0
| 3=Teamwork and WSCO*** | 189 | 189 | 189 | 315 | 315 | 315
Flow Direction | F : Supply from the front side | 0 | 0 | 0 | 0 | 0 | 0
| B : Bottom supply air to 3 sides ( front, left and right) | 215 | 265 | 345 | 358.3333 | 441.6667 | 575
| A : All side | 260 | 325 | 420 | 433.3333 | 541.6667 | 700
Shut Of Valve | 0= None | 0 | 0 | 0 | 0 | 0 | 0
| 1= Available | 386.0585 | 386.0585 | 426.0585 | 643.4308 | 643.4308 | 710.0975
| PLC Ext. Module |  |  |  |  | 153.5975